## Summary
ITEM # | INSTRUMENT TAG | DESCRIPTION | MANUFACTURER | MODEL | SERIAL NUMBER | INSTALLATION | [10 empty] | VERIFICATION OF OPERATION | [7 empty] | MISC. |  | CONTRACTOR | CONTRACT ADMINISTRATOR | CITY OF GREATER SUDBURY | DATE | NOTES/REASON(S) FOR NON-ACCEPTANCE
[6 empty] | Installation/Mounting of Sensor and Transmitter meet the design,and are in accordance with Manufacturer's recommendations | Tagging/Nameplate | Wiring/Conduit Installation, Termination and Seal | Power Supply, Circuit Breaker/Fuse Rating | Compliance Division 16 | Testing (Ground Loop, Continuity & Installation) | Check Instrument Air, Adjust Filter/Regulator | Check Temperature Control (Internal/Heat Tracing) | Instrument documentation is updated to as-built | Calibrated; Sticker with Calibration date provided on the Instrument | Manufacturer Inspection and Calibration Certificate Provided | Discrete - correct sense on operation | Discrete - correct status at PAC/RTU | Analog - Calibrated Range mA/Engineering Units | Analog - Correct Polarity at PAC | Analog - Correct span at instrument | Analog - Correct span at PAC & HMI | Analog - Correct eng. units at local display, and in HMI | Verify at 0, 50, 100 % | Verify operation Under Max. Process Conditions | Recommended spare parts have been supplied
1
2
3
4
5
6
7
8
9
10
11
12
NOTES:
1) Indicate N/A if not applicable

## Sample LIT Calibr. Report
INSTRUMENT CALIBRATION REPORT
CUSTOMER NAME: |  | City of Greater Sudbury
CONTACT NAME: |  |  |  | LOCATION:
Service Date |  |  | Manufacturer: | Milltronics
Technician: |  |  | Model: | Multiranger 100
Job #: |  |  | Serial No.: | 081402132XB
Application | Sodium Hypochlorite |  | Tag: | XXX
| INPUT DATA |  |  | DISPLAY | OUTPUT
Type: | V notch |  | Type: | Meters | Out Range ma
Min.: | 0 |  | Min.: | 0.0m | 4 mA
Max.: | 3.475 |  | Max.: | 3.475m | 20 mA
Constant: | 0
Empty Dis: | 2
|  |  |  | MA Before | Calibration |  | MA After | Calibration
Input | Disp Level | Calc. Level | Calc. Error % | Calc. O/P | As Found O/P | % Error | As left O/P | % Error
0 | 0 | 0 | 0% | 3.98 | 3.98 | -0.5% | 3.99 | 0.2513%
0.695 | 7.19 | 0 | 0% | 7.2 | 7.19 | 0% | 7.2 | -0.1389%
1.39 | 10.39 | 0 | 0% | 10.41 | 10.39 | 0.09615% | 10.4 | -0.09606%
2.085 | 13.57 | 0 | 0% | 13.59 | 13.57 | -0.07353% | 13.59 | 0%
2.78 | 16.8 | 0 | 0% | 16.79 | 16.8 | -0.05952% | 16.79 | -0.05952%
3.475 | 19.97 | 0 | 0% | 19.98 | 19.97 | -0.1% | 19.99 | -0.05%
COMMENTS
Note:
Calibration Equipment
Type: | Process Meter
Manufacturer: | Fluke
Model: | 787
Serial No.: | 838002
Last Calc. Date: | 2004-06-03 |  |  |  | Signature of Technician