WIRING IDENTIFICATION AND LABELLING

CONTENT

1	WIRING IDENTIFICATION AND LABELLING	3

2	TERMINAL AND WIRING IDENTIFICATION ON ICP WIRING DRAWINGS	3

# WIRING IDENTIFICATION AND LABELLING

The purpose of this document is to establish standards for consistent identification of wiring on the drawings and on field wiring labels.

# TERMINAL AND WIRING IDENTIFICATION ON ICP WIRING DRAWINGS

### Use different terminal symbols to identify terminal location, and include terminal symbols legend to differentiate between field device and local/starter control panels, and the ICP terminals.

### Use solid lines to represent the internal panel wiring, and dashed lines to represent the field wiring.

### All field wiring shall land on the terminals inside the ICP.

### ICP wiring identification:

#### Use circuit breaker/fuse identifier for power supply wire coming from 120VAC/24VDC power distribution to a panel device in format BBXXX, where:

##### BB stands for CB or FU for circuit breaker or fuse identification. Circuit breaker/fuse identifier is to be used in identification of power supply wires coming from ICP to instruments and devices;

##### XXX is the circuit breaker/fuse number.

#### Tag the I/O wiring as IRSSPP, or ORSSPP, where:  R is rack number, SS is slot number, and PP is a point number related to the specific I/O module, and I or O indicates input or output. For analog signals, add +/- at the end of the tag.

#### Wire tag is the same on both ends of the wire.

### ICP field cabling identification consists of source and destination identification, i.e. of the field device/panel and ICP information.  The following format is to be used for the field cabling identification:

#### AAA-TTTTLLLL-ICPNNNN-Z.

#### Where there are more than one cables with the same source and destination information, (1), (2), etc. shall be added to the cable labels.

##### AAA is the process area code (fragment 2 of the tag names);

##### TTTT is the field device (instrument/equipment/field panel) tag (fragment 3 of the device tag name);

##### LLLL is the field device (instrument/equipment/field panel) number (fragment 4 of the device tag name);

##### NNNN is an ICP number (fragment 4 of the ICP tag name);

##### Z is the cable type identification, which stands for P – power, I – instrumentation, or C – control.

### Wire identification examples:

#### Example 1: field cable between chlorination ICP number 1120 and the chemical dosing pump number 1110: DIS-MP1110-ICP1120-I.

#### Example 2: field power cable to treated water flow meter number 3011, terminal from ICP number 3001: TRW-FIT3011-ICP3001-P.

#### Example 3: field wire to treated water flow meter 3011 terminal 01 from ICP 3002 circuit breaker 0201: CB0201.

#### Example 4: signal wire from water flow meter 3011 terminal 1+ to ICP 3002 PAC rack 01, analog input 5 in module in slot 3: I10305+.